## Sheet1
Cooling‑Plant & Facility Level
Signal | Direction | Description
adjust_flow_rate | Orch → Pump | Set L/min to match transient heat loads
chiller_start | Orch → Chiller | Enable chiller to boost cooling capacity
free_cooling_mode | Orch → Economizer | Switch to outside‐air economizer
pump_flow_rate | Pump → Orch | Real‑time L/min
deltaT | Sensors → Orch | °C difference inlet→outlet
chiller_capacity_kw | Chiller → Orch | Available kW of chilled‐water cooling
chiller_start | Orch → Chiller | Boolean. Start/stop command for the main chiller.
pump_flow_rate_lpm | Chiller → Orch | Pump flow rate (L/min).
condenser_temp_C | Plant → Orch | Condenser inlet/outlet temperature (°C).
facility_deltaT_C | Plant → Orch | ΔT across the plant (°C).
chiller_capacity_kw | Chiller → Orch | Rated cooling capacity (kW).
facility_PUE | Plant → Orch | Power Usage Effectiveness = (Total Facility Power)∕(IT Equipment Power)
facility_WUE | Plant → Orch | Water Usage Effectiveness = (Water used in L)∕(IT Energy in kWh)
Server‑Node Level
Signal | Direction | Description
workload_data_announcement | Workload → BMC | Peak/baseline/ramp forecast (100 ms res) via /WDPC/workload/status
power_limit | Orch → BMC | Cap node draw to X W (throttle DVFS or pause jobs)
node_power_draw | BMC → Orch | Real‑time kW at IEC inlet via /WDPC/power/realtime
cpu_package_power | BMC → Orch | RAPL/AMDPower package draw (W)
memory_module_power | PMBus → Orch | Per‑DIMM power (W)
thermal_status | Sensors → Orch | Inlet/outlet temps, junction temps via /WDPC/thermal/status
idle_baseline_power | BMC → Orch | Measured idle draw for marginal‐compute calculations
Rack / Cabinet Level
Signal | Direction | Description
rack_power_limit | Orch → PDU | Limit branch power to X A or kW
rack_activation | Orch → PDU | Power on/off specific outlets or PDUs
pdu_branch_current | PDU → Orch | Real‑time A or kW per branch
rack_inlet_temp | Sensors → Orch | Ambient inlet °C
heat_rejection_rate | Cooler → Orch | Water L/min & ΔT °C → kW removed via /WDPC/thermal/status
rack_PUE | Infra → Orch | Derived from combined rack power & cooling signals
Networking Level
Signal | Direction | Description
net_traffic_profile | Orch → Switch | Expected Gbps/time window (for QoS or rate limiting)
port_power_cap | Orch → Switch | Cap per‑port power draw (W)
port_utilization | Switch → Orch | Real‑time Gbps per port
port_power_draw | Switch → Orch | W per port (via SFF MSA telemetry)
network_latency_alert | Switch → Orch | Over‑threshold latency notification
Power‑Infrastructure Level
Signal | Direction | Description
battery_discharge_request | Orch → UPS/BBU | Pull X kW from BBU/UPS (shave peaks)
use_generator | Orch → Generator | Spin up standby gen to X kW
demand_response_ack | Orch → Grid | Accept grid DR event
available_power_mw | Grid → Orch | MW capacity remaining
battery_soc | UPS → Orch | % state‑of‑charge
generator_status | Gen → Orch | On/off, available kW
grid_carbon_intensity | External → Orch | gCO₂/kWh forecast
External‑Systems Level
Signal | Direction | Description
request_grid_forecast | Orch → Utility | Ask for 1 h/15 min/1 min ahead load & carbon forecast
request_renewable_data | Orch → Utility | Ask for current & predicted renewables %
request_heat_network_status | Orch → Utility | Available waste‑heat uptake (kW)
renewable_available_percent | Utility → Orch | % of low‑carbon gen on‑grid
grid_status | Grid → Orch | Under/over frequency, stability alerts
heat_network_capacity | HeatNet → Orch | kW of thermal demand accepted